## Slide 1: EPICS ’Stream’ Device Support
Klemen Vodopivec based on slides from Kay Kasemir
Dec 2018

## Slide 2: What is streaming device?
Text (ASCII) bi-directional protocol
(Usually) one connection per device
Command & response
  What is the current temperature on channel A?
  KRDG A?
  Reply
  +077.350E+0\n
Serial (RS-232, RS485), Networked (TCP), GPIB (IEEE-488)
EPICS device called StreamDevice

## Slide 3: Examples
Temperature controllers
  Lakeshore
  Omega
  …
Vacuum pumps
  Varian
  …
Power supplies
  Agilent
  Spellman
  …
Moxa (modbus, profinet, serial, etc.)

## Slide 4: Pro/Cons
Seems easy
  Human-readable
  Testable with minicom, telnet
  Create Visual Basic, LabVIEW, Python … demo in no time
But beware!
  Speed and Terminators (CR, LF, CR/LF, …) can magically change
    Was set to something, than device power-cycled …
  Must handle timeouts
    Don’t just hang!
  Must handle errors
    Don’t read “MODEL 340” as 340 Kelvin

## Slide 5: EPICS StreamDevice Idea
Protocol File “demo.proto” Terminator = CR; getTempA { out "KRDG? A"; in "%f"; }
Record record(ai, "Temp:B") { field(DTYP,"stream") field(INP, "@demo.proto getTempA TC1") field(SCAN,"5 second") }
IOC st.cmd drvAsynIPPortConfigure ("TC1", "192.168.164.10:23")

## Slide 6: EPICS StreamDevice features
EPICS integration
Connection management through asyn
  Automatically connect
  Re-connect after disconnects
Allow many records to communicate via one connection
  Threading, queuing, …
Handle timeouts, errors
  Put records into ‘alarm’ state
Debug options
  Log every byte sent/received

## Slide 7: Adding StreamDevice support to IOC
configure/RELEASE or RELEASE.local: ASYN=/path/to/asyn STREAM=/path/to/StreamDevice
demoApp/src/Makefile demo_DBD += stream.dbd demo_DBD += asyn.dbd demo_DBD += drvAsynIPPort.dbd demo_LIBS += asyn demo_LIBS += stream

## Slide 8: EPICS Database
record(ai, "B") { field (DTYP, "stream") field (INP, "@demo.proto getB NC") field (SCAN, "5 second") } record(ai, "A") { field (DTYP, "stream") field (INP, "@demo.proto getA NC") field (SCAN, "I/O Intr") }
record(ao, "current") { field (DTYP, "stream") field (OUT, "@demo.proto setCurrent NC") field (EGU, "A") field (PREC, "2") field (DRVL, "0") field (DRVH, "60") field (LOPR, "0") field (HOPR, "60“) }
stream-demo.db

## Slide 9: Protocol File
Terminator = CR LF; InTerminator = LF; ReplyTimeout = 10000; ReadTimeout = 10000;
# Used with SCAN “… second” – # triggered from DB record. # Prompts, then expects "B 5" getB { out "B?"; in "B %f“; @mismatch { disconnect; } }
# Used with SCAN, "I/O Intr”. # Reacts to "A 5" at any time getA { PollPeriod = 50; in "A %f"; }
# Example with initialization, # otherwise only writes when processed setCurrent { out "CURRENT %.2f"; @init { out "CURRENT?"; in "CURRENT %f A"; } }
stream-demo.proto
System variables

## Slide 10: Protocol File
Terminator = CR LF; InTerminator = LF; ReplyTimeout = 10000; ReadTimeout = 10000;
# Used with SCAN “… second” – # triggered from DB record. # Prompts, then expects "B 5" getB { out "B?"; in "B %f“; @mismatch { disconnect; } }
# Used with SCAN, "I/O Intr”. # Reacts to "A 5" at any time getA { PollPeriod = 50; in "A %f"; }
# Example with initialization, # otherwise only writes when processed setCurrent { out "CURRENT %.2f"; @init { out "CURRENT?"; in "CURRENT %f A"; } }
stream-demo.proto
Comment

## Slide 11: Protocol File
Terminator = CR LF; InTerminator = LF; ReplyTimeout = 10000; ReadTimeout = 10000;
# Used with SCAN “… second” – # triggered from DB record. # Prompts, then expects "B 5" getB { out "B?"; in "B %f“; @mismatch { disconnect; } }
# Used with SCAN, "I/O Intr”. # Reacts to "A 5" at any time getA { PollPeriod = 50; in "A %f"; }
# Example with initialization, # otherwise only writes when processed setCurrent { out "CURRENT %.2f"; @init { out "CURRENT?"; in "CURRENT %f A"; } }
stream-demo.proto
Function definition and implementation in curly brackets

## Slide 12: Protocol File
Terminator = CR LF; InTerminator = LF; ReplyTimeout = 10000; ReadTimeout = 10000;
# Used with SCAN “… second” – # triggered from DB record. # Prompts, then expects "B 5" getB { out "B?"; in "B %f“; @mismatch { disconnect; } }
# Used with SCAN, "I/O Intr”. # Reacts to "A 5" at any time getA { PollPeriod = 50; in "A %f"; }
# Example with initialization, # otherwise only writes when processed setCurrent { out "CURRENT %.2f"; @init { out "CURRENT?"; in "CURRENT %f A"; } }
stream-demo.proto
Commands
out for send
in for receive
Other commands:
wait
event
connect
disconnect
exec

## Slide 13: Protocol File
Terminator = CR LF; InTerminator = LF; ReplyTimeout = 10000; ReadTimeout = 10000;
# Used with SCAN “… second” – # triggered from DB record. # Prompts, then expects "B 5" getB { out "B?"; in "B %f“; @mismatch { disconnect; } }
# Used with SCAN, "I/O Intr”. # Reacts to "A 5" at any time getA { PollPeriod = 50; in "A %f"; }
# Example with initialization, # otherwise only writes when processed setCurrent { out "CURRENT %.2f"; @init { out "CURRENT?"; in "CURRENT %f A"; } }
stream-demo.proto
Format converters start with % - similar to printf() syntax
%f for floating point number

## Slide 14: Protocol File
Terminator = CR LF; InTerminator = LF; ReplyTimeout = 10000; ReadTimeout = 10000;
# Used with SCAN “… second” – # triggered from DB record. # Prompts, then expects "B 5" getB { out "B?"; in "B %f“; @mismatch { disconnect; } }
# Used with SCAN, "I/O Intr”. # Reacts to "A 5" at any time getA { PollPeriod = 50; in "A %f"; }
# Example with initialization, # otherwise only writes when processed setCurrent { out "CURRENT %.2f"; @init { out "CURRENT?"; in "CURRENT %f A"; } }
stream-demo.proto
Exception handling
mismatch
writetimeout
replytimeout
readtimeout

## Slide 15: Protocol File
Terminator = CR LF; InTerminator = LF; ReplyTimeout = 10000; ReadTimeout = 10000;
# Used with SCAN “… second” – # triggered from DB record. # Prompts, then expects "B 5" getB { out "B?"; in "B %f“; @mismatch {
# Commented out for demo #disconnect; } }
# Used with SCAN, "I/O Intr”. # Reacts to "A 5" at any time getA { PollPeriod = 50; in "A %f"; }
# Example with initialization, # otherwise only writes when processed setCurrent { out "CURRENT %.2f"; @init { out "CURRENT?"; in "CURRENT %f A"; } }
stream-demo.proto

## Slide 16: IOC Startup File
epicsEnvSet ("STREAM_PROTOCOL_PATH", ”path/to/proto/files")
drvAsynIPPortConfigure ("NC", "127.0.0.1:6543")
# Log some asyn info and in/out texts # ASYN_TRACE_ERROR 0x0001 # ASYN_TRACEIO_DEVICE 0x0002 # ASYN_TRACEIO_FILTER 0x0004 # ASYN_TRACEIO_DRIVER 0x0008 # ASYN_TRACE_FLOW 0x0010 # ASYN_TRACE_WARNING 0x0020 asynSetTraceMask("NC", 0, 4) asynSetTraceIOMask("NC", 0, 6)
dbLoadRecords("db/stream-demo.db","user=fred")
iocBoot/iocdemo/st.cmd

## Slide 17: Example Session
B?
2018/12/04 16:18:11.519 NC wrote
B?\r\n
42 3f 0d 0a
IOC console output
NetCat interactive demo
‘nc -l 127.0.0.1 6543

## Slide 18: Example Session
B?
B 12
2018/12/04 16:18:11.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:11.902 NC read
B 12\n
42 20 31 32 0a
IOC console output
NetCat interactive demo
‘nc -l 127.0.0.1 6543

## Slide 19: Example Session
B?
B 12
B?
2018/12/04 16:18:11.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:11.902 NC read
B 12\n
42 20 31 32 0a
2018/12/04 16:18:16.519 NC wrote
B?\r\n
42 3f 0d 0a
IOC console output
NetCat interactive demo
‘nc -l 127.0.0.1 6543

## Slide 20: Example Session
B?
B 12
B?
B 3.14
2018/12/04 16:18:11.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:11.902 NC read
B 12\n
42 20 31 32 0a
2018/12/04 16:18:16.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:16.875 NC read
A 3.14\n
41 20 33 2e 31 34 0a
IOC console output
NetCat interactive demo
‘nc -l 127.0.0.1 6543

## Slide 21: Example Session
B?
B 12
B?
B 3.14
B?
2018/12/04 16:18:11.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:11.902 NC read
B 12\n
42 20 31 32 0a
2018/12/04 16:18:16.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:16.875 NC read
A 3.14\n
41 20 33 2e 31 34 0a
2018/12/04 16:18:21.519 NC wrote
B?\r\n
42 3f 0d 0a
IOC console output
NetCat interactive demo
‘nc -l 127.0.0.1 6543

## Slide 22: Example Session
B?
B 12
B?
B 3.14
B?
2018/12/04 16:18:11.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:11.902 NC read
B 12\n
42 20 31 32 0a
2018/12/04 16:18:16.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:16.875 NC read
A 3.14\n
41 20 33 2e 31 34 0a
2018/12/04 16:18:21.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:31.529 NC B: No reply from device within 10000 ms
IOC console output
NetCat interactive demo
‘nc -l 127.0.0.1 6543

## Slide 23: Example Session
B?
B 12
B?
B 3.14
B?
B?
2018/12/04 16:18:11.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:11.902 NC read
B 12\n
42 20 31 32 0a
2018/12/04 16:18:16.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:16.875 NC read
A 3.14\n
41 20 33 2e 31 34 0a
2018/12/04 16:18:21.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:31.529 NC B: No reply from device within 10000 ms
2018/12/04 16:18:36.519 NC wrote
B?\r\n
42 3f 0d 0a
IOC console output
NetCat interactive demo
‘nc -l 127.0.0.1 6543

## Slide 24: Example Session
B?
B 12
B?
B 3.14
B?
B?
34
2018/12/04 16:18:11.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:11.902 NC read
B 12\n
42 20 31 32 0a
2018/12/04 16:18:16.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:16.875 NC read
A 3.14\n
41 20 33 2e 31 34 0a
2018/12/04 16:18:21.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:31.529 NC B: No reply from device within 10000 ms
2018/12/04 16:18:36.519 NC wrote
B?\r\n
42 3f 0d 0a
2018/12/04 16:18:36.893 NC read
34\n
33 34 0a
2018/12/04 16:18:36.893 NC B: Input "34" mismatch after 0 bytes
2018/12/04 16:18:36.893 NC B: got "34" where "B " was expected
IOC console output
NetCat interactive demo
‘nc -l 127.0.0.1 6543

## Slide 25: More in StreamDevice Manual (online)
21 supported EPICS records
  Including waveform
Value skipping (ie. ROI %*d %d)
Multi-line messages
Format converters
Settings aka System variables
http://epics.web.psi.ch/software/streamdevice/doc/index.html

## Slide 26: And asyn for connection details
drvAsynSerialPortConfigure
  Baud, bits, parity, stop etc.
drvAsynIPPortConfigure
  Hostname and port
asynGpib
https://epics.anl.gov/modules/soft/asyn/R4-34/asynDriver.html
https://epics.anl.gov/modules/soft/asyn/R4-34/HowToDoSerial/HowToDoSerial_StreamDevice.html

## Slide 27: StreamDevice…
Allows you to concentrate on the protocol
Handles the rest
  Connection
  Threads
  Parse results
  Update record’s value and alarm state
“demo.proto” Terminator = CR; getTempA { out "KRDG? A"; in "%f"; }