## Slide 1: Archive
Oct. 2018
Kay Kasemir

## Slide 2: Idea
IOC
CA Server
PVA Server
Archiver

## Slide 3: Practice
Storage Tons of fast storage
Archive Engine (Service)
Read PVs, write to storage
CA, PVA
Configuration:
Which channels? How?
IOC

## Slide 4: Choices…
Channel Archiver: XML config, custom file storage
  Fast
  Fragile
  Data access via C++ library & web service
  Can’t be maintained as setup grows
RDB: RDB for both config and storage
  Slow
  Robust
  Access from any piece of code
  Very maintainable for decades
SLAC Archiver Appliance: RDB config, custom protobuf storage
  Fast
  Robust?
  Web service
  Maintainable over time?

## Slide 5: IOC Configuration
Archive engines subscribe to “archive” events (DBE_ARCHIVE)
  camonitor –m l the_pv_name
For analog records, configure the ADEL field
  Unfortunately not perfect for ‘log’ type values like vacuum pressures
Assert that your IOC knows the time
  Check time stamps reported by camonitor

## Slide 6: Archive Engine Options
Monitor
  Tries to save every received update
  Based on ADEL
  Might need an expected-update-rate to allocate buffers, skipping samples if there are too many
Scan
  Writes the most recent value every N seconds
  Stores original time stamps

## Slide 7: Setup of RDB Archive
See phoebus online help or https://github.com/shroffk/phoebus/blob/master/services/archive-engine/doc/index.rst
Install MySQL
Setup archive tables

## Slide 8: Configure RDB Archive
cd ~/epics-train/examples/archive/
archive_engine -help
archive_engine -list
archive_engine -engine Demo -export `pwd`/Demo.xml
archive_engine -engine Fishtank -import `pwd`/Fishtank.xml
archive_engine -engine Fishtank –settings my_settings.ini
Check http://localhost:4812 in web browser

## Slide 9: Viewing Archived Data
Open Data Browser, add PV
Data Browser Preferences:
org.csstudio.trends.databrowser3/urls=jdbc:mysql://localhost/archive|RDB org.csstudio.trends.databrowser3/archives=jdbc:mysql://localhost/archive|RDB org.csstudio.trends.databrowser3/use_default_archives=true

## Slide 10: Archive
Fundamentally simple: Store values of PVs
There is no perfect implementation
  Can’t store everything at high rate forever
Looking at data in Data Browser is easy