## Slide 1: EPICS 7
Kay Kasemir, June 2019

## Slide 2: EPICS 7 =
Available since Dec. 2017
EPICS ‘base’
Records, Device Support,
Channel Access, softIoc
Almost like R3.13 from 1994
EPICS ‘V4’
PVAccess,
softIocPVA Started ~2010
+

## Slide 3: EPICS 7 ?
Revolutionizes EPICS
Everything is
  Easier
  Faster
  More colorful
  Service-oriented
Kills EPICS as you know it
  Services replace IOCs
  Channel Access clients no longer connect
  Breaks your device support
  Needs more CPU & Memory

## Slide 4: Now What?
Use EPICS as before
  No need to change anything
  Look at ‘RELEASE.local’ mechanism
  Support for 64bit numbers, SMP, locking tweaks
Start to use PV Access
  Images
  Custom structures
Transition everything to PV Access
  .. Once there’s a PVA Gateway, access security, everything “works”

## Slide 5: EPICS Base
Records, device support, databases, sequences, … as before
Modules encouraged to use RELEASE.local
XXX/configure/RELEASE
ASYN=/path/to/asyn1-2-3 EPICS_BASE=…
XXX/configure/RELEASE
-include $(TOP)/../RELEASE.local
RELEASE.local
ASYN=/path/to/asyn1-2-3 AUTOSAVE=/path/to/auto1-2-3 … EPICS_BASE=…
YYY/configure/RELEASE
AUTOSAVE=/path/to/auto1-2-3 EPICS_BASE=…
YYY/configure/RELEASE
-include $(TOP)/../RELEASE.local

## Slide 6: RELEASE.local in Training Setup
cd ~/epics-train/tools
ls –d base* seq* asyn*
cat RELEASE.local
cat seq*/configure/RELEASE

## Slide 7: PV Access
How does it differ from Channel Access?
How do I…
  … add PVA to an IOC?
  … ‘caget’ with PVA?
  … use PVA in UI tools (Operator Displays, ..)?
Area Detector: Any advantage using PVA?
Custom Data: Any advantage using PVA?
Some Python Examples

## Slide 8: History
Channel Access
  Since beginning of EPICS
  DBR_*: Numbers, enums, string, scalar and array, with time, alarm, limits
  Still fully supported
PV Access
  Started as “EPICS V4” development
  PV Data: Arbitrary structures
  Since EPICS 7 (Dec. 2017) included in EPICS base

## Slide 9: Review Channel Access
cd ~/epics-train/examples/first_steps cat first.db softIoc –m S=training –d first.db
echo $EPICS_CA_ADDR_LIST caget training:random camonitor training:random
cainfo training:random caget –h caget –d DBR_CTRL_DOUBLE training:random
cainfo training:random.SCAN caget –d DBR_CTRL_ENUM training:random.SCAN

## Slide 10: How Clients find Channels
Client
Client
Client
Client
Client
Client
IOC
IOC
IOC
Meter
Power Supply
Camera
IOC
Channel Access
Has PV "PS1:Voltage"
Wants to read "PS1:Voltage"

## Slide 11: Important Environment Variables
EPICS_CA_ADDR_LIST
  Determines where to search
  Is a list (separated by spaces)
    “123.45.1.255 123.45.2.14 123.45.2.108”
  Default is broadcast addresses of all interfaces on the host
    Works when servers are on same subnet as Clients
  Broadcast address
    Goes to all servers on a subnet
    Example: 123.45.1.255
    Use `ifconfig –a` on UNIX to find it
EPICS_CA_AUTO_ADDR_LIST
  YES: Include default addresses above in searches
  NO: Do not search on default addresses
  If you set EPICS_CA_ADDR_LIST, usually set this to NO

## Slide 12: Channel Properties
Each channel comes with properties:
  Value
    of type string or double or int or …
    Scalar or array
  Time stamp
    Up to nanosecond precision
  Severity code
    OK, MINOR, MAJOR, or INVALID
  Status code to qualify the severity
    OK, READ error, WRITE error, at HIGH limit, …
  units, suggested display range, control limits, alarm limits.

## Slide 13: Client interface to properties
The available properties are fixed.
  One cannot add a new 'color' property.
The request types are fixed.
  "DBR_…" types.
  Available:
    Just value.
    Value with status and severity.
    Value with status, severity and time stamp.
    Almost Everything: Value, units, status, limits, … but time
  Not available:
    Custom combinations like value, precision, units.
  See `caget –h`

## Slide 14: Example: AI record "fred"
PV "fred" or "fred.VAL"
  value property of channel = VAL field of record.
    Type double, one element (scalar).
  time property = TIME field
  status = STAT
  Severity = SEVR
  units = EGU
  Precision = PREC
  display limit low, high = LOPR, HOPR
  control limit low, high = LOPR, HOPR
  alarm limits = LOLO, LOW, HIGH, HIHI
Makes a lot of sense.
  GUI can display the value together with units, formatted according to the precision, as e.g. "12.37 volts”.

## Slide 15: Example: AI record "fred"
PV "fred.SCAN"
  value property of channel = SCAN field of record.
    Type enumerated, values: "Passive", "1 second", ...
  time property = TIME field?
  status = STAT?
  Severity = SEVR?
  control limit low, high = 0, ??

## Slide 16: How is PV Access different?
cd epics-train/examples cat first.db softIocPVA –m S=training –d first.db
echo $EPICS_PVA_ADDR_LIST pvget training:random pvmonitor training:random pvget –m training:random
pvinfo training:random pvinfo training:random.SCAN

## Slide 17: Channel Access vs. PV Access
Similar command line tools:
pvinfo training:ai1
pvget training:ai1
pvmonitor training:ai pvget –m training:ai1
pvget –v -r 'field()' training:ai1
pvget training:ai1.SCAN
﻿start_iocExample
cainfo training:ai1
caget training:ai1
camonitor training:ai1
caget –d CTRL_DOUBLE training:ai
caget training:ai1.SCAN

## Slide 18: PV Access
Fundamentally similar to Channel Access
  Name search via UDP
  Connection for data transfer via TCP
  EPICS_PVA_ADDR_LIST, EPICS_PVA_AUTO_ADDR_LIST
Get, put, monitor
  Plus ‘GetPut’, ’PutGet’, ‘RPC’ type operations
Arbitrary PV Data structures instead of DBR_.. types

## Slide 19: Arbitrary Data: Great, but then what?
structure: double value short status short severity string units time timeStamp …
structure: short level double data string type time stamp …
structure: short info double content string meta long ms …
Which number to show on a user display?
What units?
Is this an alarm?
Time stamp?
structure: short level double wert string typ long zeit …

## Slide 20: “Normative Types”
Channel Access
struct dbr_ctrl_double: short status short severity short precision char units[8] … no timestamp … double value struct dbr_time_double: short status short severity timestamp stamp double value
You get what you request (network always transfers complete struct)
PV Access
epics:nt/NTScalar: double value short status short severity string units time timeStamp …
You get what you request (but network only transfers changes)

## Slide 21: Channel Access vs. PV Access in UI Tools

## Slide 22: Getting Started with CSS
Start `css`

## Slide 23: Probe
Open Menu Applications, Display, Probe
Enter PV name “sim://sine”
Open another Probe for “training:random” (or some other PV from your IOC)
Close Probe
Open it again
Note previously used PVs in history as you enter new PV
Right-click on the “Probe” tab, Select “Split Horizontally”, and move one of the probes to new panel.

## Slide 24: Data Browser
Menu Applications, Display, Data Browser
Right-click on plot, Add PV, “sim://sine”
Wait a little, press Stagger button, then zoom and select a region on the time axis

## Slide 25: PV Tree
Menu Applications, Display, PV Tree
Enter a PV from an IOC, like “training:random”

## Slide 26: CSS PV Exchange
PV in any CSS Tool  Context Menu  Select other PV Tool
Try:
Right-click on item in PV Tree, select Data Browser

## Slide 27: CS-Studio: Use ‘pva://…’
For now, just “pvname” is same as “ca://pvname”. “pva://” selects PV Access. Eventually, that could become the default.

## Slide 28: Create New Display
Menu Applications, Display, New Display
  Enter a name with .bob file extension
Main Editor Area Select Widgets Move, resize widgets Ctrl-C, V, X to copy, paste, delete (⌘ on Mac)
Save & Execute the Display
Property Panel Edit properties of selected widgets

## Slide 29: Editing a Display
Quick Edit Double-click widget to
a) Edit text of Label
b) Edit PV of widgets that use a PV
Widget Palette Drag widget into editor
- or -
1) Select Widget Type
2) Draw rectangular area in display
Selecting Widgets a) Click single widget
b) Ctrl-click to add widget (⌘ on Mac)
c) Drag ‘rubberband’ around widgets
d) Click or Ctrl/ ⌘ click in widget list

## Slide 30: Extend the First Display
Drag a “Text Update” from the palette
  Enter PV name “sim://ramp(1, 10, 1)”. Note PV name auto-completion popup.
Add “Boolean Button”
  PV name “loc://test”
Add “LED”
  PV name “loc://test”. Note name in PV History.
Execute the display
  Toolbar Button or Context Menu

## Slide 31: Browse the Display Examples
Training setup: Open /home/training/epics-train/examples/Display Builder/01_main.bob
  Fresh CS-Studio Setup: Applications, Display, Examples, Install Example Displays
Context Menu: Open in Editor to inspect how it’s done
Try all of them..

## Slide 32: How is PV Access different? Images!
start_imagedemo pvinfo IMAGE # CSS displays/PVA_Image.bob

## Slide 33: Area Detector
Disclaimer:
This will only scratch the surface.
EPICS web site has several days of training material if you are serious about using the A.D.

## Slide 34: Area Detector
EPICS framework for image manipulation
Detectors/Cameras
  Cheap “Web Cam”
  $$$ high speed, high res.
  Neutron, X-Ray detectors
Plugins collection
  ROI
  Transform
  ColorConvert
  Etc.

## Slide 35: ADSimDetector
Simulated images
  cd ~/epics-train/examples/AreaDetector ./start_sim_ioc.sh
Open the AreaDetectorDemo.bob
  On “Detector” page, “Start” the SIM1 detector
  By itself, this creates an Area Detector port “SIM1”. To see it, need to publish via CA or PVA

## Slide 36: NDPluginStdArrays
Serves image as Channel Access waveform
On Detector, Plugins, All, find NDPluginStdArrays
  Port = “SIM1”
  Enable
AreaDetectorDemo.bob shows image
  PV: 13SIM1:image1:ArrayData
  Width x Height: 1024 x 1024
  Unsigned

## Slide 37: NDPluginOverlay
Adds rectangles, text etc. to image
On Detector, Plugins, All, find NDPluginOverlay “OVER1”
  Set its Port to “SIM1”, Enable
  Change NDPluginStdArrays’s Port to “OVER1”
  Press “More”, select first of the “Individual Overlays”

## Slide 38: NDPluginOverlay.. Overlay #1
Set Use: Yes, Shape: Rectangle, set X and Y as shown

## Slide 39: What we did
Area Detector IOC
SIM1
OVER1
Image1
Driver
Plugins
OVER1 offers 8 overlays:
Rectangle
Text “Hello”
…

## Slide 40: Many More Plugins…
Process
  Background subtraction, clipping, recursive averaging over N images, ..
Saving images in various formats
  Adding data from PVs as “Attributes”
  PNG, JPEG, TIFF, HDF5, …
Serving NDArray via PVA
  For displays: No need to configure size, data type, …
  For ADPvAccess Driver: Process data on different hosts

## Slide 41: NDPluginPVA – Serve PVA ‘Image’
In Plugins, “PVA1”
  Set its Port to “SIM1” or “OVER1”, Enable
PVAccess Tests
  pvinfo 13SIM1:Pva1:Image
  pvget -r 'dimension' 13SIM1:Pva1:Image
In Display
  Use “Image” widget
  Set PV
  No need to configure data size, data type

## Slide 42: NDPluginPVA – Serve PVA ‘Image’
Display adapts to image size

## Slide 43: How is PV Access different? Custom Data!

## Slide 44: Custom PV Data
SNS Beam Lines started to use this in ~2014
  start_neutrondemo
  pvinfo neutrons
Allows fetching just what’s needed:
  # For detector pixel display pvget -r 'field(pixel)' neutrons pvget –m -r 'field(timeStamp, pixel)' neutrons
  # For energy displays pvget –m -r 'field(time_of_flight, pixel)' neutrons

## Slide 45: Custom PV Data in CS-Studio
Cannot handle arbitrary structure
  pva://neutrons
Can handle fields which are scalar or array
  pva://neutrons/proton_charge
  pva://neutrons/pixel

## Slide 46: Custom PV Data from IOC Records
`makeBaseApp.pl –t example` includes “group”, see ~/epics-train/examples/ExampleApp/Db/circle.db
  Calc records ..:circle:x & ..:circle:y compute (x, y) coordinate on circle
  info() annotations create PV ”training:circle” PV as struct { angle, x, y }
PVA “training:circle” updates atomically
  camonitor training:circle:x training:circle:y separate x, y updates pvget –m training:circle will always see sqrt(x2+y2)==1
  cd ~/epics-train/examples/python python circle.py

## Slide 47: Python

## Slide 48: PV Access and Python
start_iocExample
Basic ‘get’
  cd ~/epics-train/examples/python/
  python example1.py
‘monitor’
  python example2.py

## Slide 49: Custom PV Data in Python Client
Python receives data as dictionary, access to any element
  python neutrons.py

## Slide 50: Custom PV Data from Python Server
Surprisingly easy:
  # Server
  python server.py
  # Client
  pvinfo pair
  pvget -m -r "x, y" pair
pv = PvObject({'x': INT, 'y' : INT})
server = PvaServer('pair', pv)
x = 1
while True:
pv['x'] = x
pv['y'] = 2*x
server.update(pv)
sleep(1)
x = x + 1

## Slide 51: More Examples
Display Builder pva_server_ramp
  Python code that serves ‘pva://ramp’ with alarm, prec, timestamp, …
Display Builder table_server
  Python code that serves ‘pva://table’ as “NTTable”
  Impractical to replace all regular IOCs with python, but useful when custom data is needed

## Slide 52: Ongoing Work
PVA Gateway
Access Security
Normative Type details: ‘format’, precision, …
Database: Support PVA links. field(INP, “pva://other_record”)

## Slide 53: EPICS 7
EPICS ‘base’
Records, Device Support,
Channel Access, softIoc
EPICS ‘V4’
PVAccess,
softIocPVA
+
No need to worry about existing R3.x setups
You may start using PVAccess
  Images
  Custom Data
Good Python support
CS-Studio is one of the early ‘bilingual’ tools