## Slide 1: Autosave
Kay Kasemir
Feb. 2022

## Slide 2: Purpose of “autosave” (aka. ‘bumpless save/restore’)
Values of some EPICS Records need to persist across IOC reboots
  ‘Set points’ entered by user
  Current ‘positions’ of motors*
* Fine print: In some cases, the hardware can do this: PLC, Parker6k, ... At IOC startup, Device support ‘init()’ should then read from hardware. But what if the hardware lost the settings? Who’s in charge here?? Need to think about this case-by-case!

## Slide 3: How To Use
Add ‘autosave’ module to IOC
Configure what to persist

## Slide 4: Add Autosave to IOC
Define path in configure/RELEASE or ../RELEASE.local:
  AUTOSAVE=/home/controls/epics/…/autosave-R5-9
Add binary and DBD info to xyzApp/src/Makefile: YourProduct_DBD += asSupport.dbd YourProduct_LIBS += autosave
Use the support module in the IOC startup file: cd ${AUTOSAVE} # Optional database for autosave status dbLoadRecords "db/save_restoreStatus.db", "P=$(IOCNAME):” # Configure (more later) set_requestfile_path("/home/controls/var”) create_monitor_set(..)

## Slide 5: Specify What to Save
Add annotations to the EPICS database:
record(type, "$(S):SomeRecord") { info(autosaveFields, "VAL LOW") field(LOW, "-10") ..
  Ultimately, autosave needs a file somefile.req that lists what to persist. Could create that manually, but suggested approach is to create from EPICS database annotations.

## Slide 6: IOC Startup
# Configure file locations epicsEnvSet IOCNAME MyIOCName epicsEnvSet SAVE_DIR /home/controls/var/$(IOCNAME)
set_requestfile_path("$(SAVE_DIR)") set_savefile_path("$(SAVE_DIR)")
# If loading save_restoreStatus.db save_restoreSet_status_prefix("$(IOCNAME):")
# Schedule a maximum of 3 sequenced backups of the .sav file # every 10 minutes - .sav0, .sav1, .sav2 save_restoreSet_NumSeqFiles(3) save_restoreSet_SeqPeriodInSeconds(600)
# Arrange for restoring saved values into records set_pass1_restoreFile("$(IOCNAME).sav")
# Start IOC processes iocInit
# Create request file and start periodic 'save’ makeAutosaveFileFromDbInfo("$(SAVE_DIR)/$(IOCNAME).req", "autosaveFields")
create_monitor_set("$(IOCNAME).req", 30)

## Slide 7: Autosave
Some boilerplate for initial setup
Later, when adding records, remember “info(autosaveFields, VAL)”
 IOC now restarts with previously saved values

## Slide 8: Autosave Documentation
http://htmlpreview.github.io/?https://github.com/epics-modules/autosave/blob/R5-7-1/documentation/autoSaveRestore.html
Important nuances Section 8 – Notes on restore passes
Section 10 – Save file details