## Slide 1: CA/PVA Channel vs. IOC Record vs. Python CAS/PVA server
Kay Kasemir, Feb. 2022

## Slide 2: What is a Process Variable?
Good question!
"A named piece of data with attributes”

## Slide 3: Channel Properties (= Data in a Process Variable)
Each channel comes with properties:
  Value
    String, double, int or …
    Scalar or array
  Time stamp
    Up to nanosecond precision
  Severity code
    OK, MINOR, MAJOR, or INVALID
  Status code to qualify the severity
    OK, READ error, WRITE error, at HIGH limit, …
  Units, suggested display range, control limits, alarm limits.
CA: Client uses ‘request’ type to select what it needs PVA: Client gets everything, then changes

## Slide 4: What is a PV (Channel)?
Whenever there's a CA/PVA server out there which decides to respond to a search request, that's a PV!
IOC responds to "record.field"
  Almost every field of every record is a PV
  There’s a mapping from record fields to channel properties (you might need to read the source code of the specific record for full detail)
Alternatively, your python code creates the PVs and sets the channels’ properties
  Nobody will know what you decide to put there

## Slide 5: What is a Process Variable?
Analog Record (ai, calc, …)
Fields
  VAL
  DESC
  EGU
  PREC
  LOPR, HOPR
  LOLO, LOW, HIGH, HIHI
  TIME
Channel
DBR_CTRL_DOUBLE or NT_Scalar
  value
  status/severity
  time stamp
  units
  precision
  display limits
  warn limits
  alarm limits
  ctrl limits
My Python Program
from p4p.server import …
…
?

## Slide 6: Consider this Record
record(calc, "t1:calcExample") { field(DESC, "Sawtooth Ramp") field(SCAN, "1 second") field(CALC, "(A<10)?(A+1):0") field(INPA, "t1:calcExample.VAL") field(PREC, "2") field(EGU, ”steps") field(LOPR, "0") field(HOPR, "10") field(HIGH, "8") field(HIHI, "9") }
t1:calcExample as DBR_CTRL_DOUBLE
  value = VAL
  status/severity = STAT/SEVR
  Units = EGU
  Precision = PREC
  display limits = LOPR/HOPR
  warn limits = LOW/HIGH
  alarm limits = LOLO/HIHI
  ctrl limits = LOPR/HOPR
t1:calcExample.DESC or CALC as DBR_TIME_STRING
  value = DESC
  status/severity = STAT/SEVR
  time stamp = TIME
t1:calcExample.SCAN as DBR_CTRL_ENUM
  value = SCAN
  status/severity = STAT/SEVR
  labels = [ “Passive”, .., “10 second”, .., “.1 second”]
t1:calcExample as DBR_TIME_DOUBLE
  value = VAL
  status/severity = STAT/SEVR
  time stamp = TIME

## Slide 7: Example: AI record "fred"
PV "fred" or "fred.VAL"
  value property of channel = VAL field of record.
    Type double, one element (scalar).
  time property = TIME field
  status = STAT
  Severity = SEVR
  units = EGU
  Precision = PREC
  display limit low, high = LOPR, HOPR
  control limit low, high = LOPR, HOPR
  alarm limits = LOLO, LOW, HIGH, HIHI
Makes a lot of sense.
  GUI can display the value together with units, formatted according to the precision, as e.g. "12.37 volts”.

## Slide 8: Example: AI record "fred"
PV "fred.SCAN”, read as a number
  value property of channel = Enum index of record’s SCAN value
    0 for "Passive", 1 for “Event”, .., 6 for "1 second", ..
  time property = TIME field
  status = STAT
  Severity = SEVR
  units = EGU
  Precision = 0
  display limit low, high = 0, ??
  control limit low, high = 0, ??
  alarm limits = 0, 0, 0, 0
Makes some sense, but
  Units don't really apply to the SCAN field.
  Its value range is really limited by the available SCAN choices, not 0..??.

## Slide 9: Channel Access vs. PV Access
Original EPICS network protocol
Typically used with IOCs & records
  You get what the records provide
The request types are fixed.
  Predefined "DBR_…" types
    Just value.
    Value with status and severity.
    Value with status, severity and time stamp.
    "Everything:" value, units, time, status, limits, …
  Client always gets the full requested DBR_.. Data
  Cannot ask for custom combination like value, units, seconds of time stamp.
With your own CA server, you cannot support new properties like ‘color’.
Alternate network protocol since ~2015
Can be used with same IOCs and records
  You get what the records provide
You can request anything
  Suggested “Normative Types”
    Same concept as DBR_.. types
  Optimized: Under the hood, only changes are sent to client
  Can ask for custom combination like value, unit, seconds of time stamp.
With your own PVA server, you can support new properties like ‘color’.

## Slide 10: Key Points
Channel != Record
  IOC maps fields of records to properties of channel
  This separation allowed development of generic clients (displays, alarm tools, archives) independent from IOCs
There is a growing number of non-IOC CA servers
  pcaspy, …
  They provide channels “x” with value, units, precision, alarms, time.. but that doesn’t mean you can read/write “x.EGU”, “x.PREC”, … There is no record!
PVAccess allows custom data types
  But to remain compatible, try to support the Normative Types