## Slide 1: “Sequencer”, State Notation Language SNL
Kay Kasemir,
Many slides from Andrew Johnson, APS/ANL
Feb. 2022

## Slide 2: EPICS Sequencer
Implementation of the state transition control model
Transparently supports channel access connections
  Read connection state of PVs
  Get and put values
  Monitor value changes
SNL – State Notation Language
  Syntax for describing a state machine
  Generates C code and supports insertion of manually crafted blocks of code
    %% strcpy( seqg_var->stateName, "init" ); %{ // multiple lines of c or c++ code }%
  Produces compiled code

## Slide 3: IOC
Channel Access
LAN
Sequencer
Device Support
I/O Hardware
IOC
Database
Database: Data Flow, mostly periodic processing
Sequencer: State machine, mostly on-demand
Optional: Sequencer runs as standalone CA-Client
CA Client
Sequencer

## Slide 4: State Machine 101
State A
State B
Event
Action
Transition
A to B
System is in some state
Events trigger transitions to other states
Actions may be performed on transition

## Slide 5: Example
Start
Poor vacuum
Good vacuum
pressure < 5.1 uTorr
Open the valve, update pumps, …
pressure > 4.9 uTorr
Close the valve, update pumps, …

## Slide 6: Example State Notation Language
state poor_vacuum {
when (pressure <= .0000049) {
RoughPump = 0;
pvPut(RoughPump);
CryoPump = 1;
pvPut(CryoPump);
Valve = 1;
pvPut(Valve);
} state good_vacuum
}
state good_vacuum
{
…
State
Event
Action
Transition

## Slide 7: How it works
State Notation Language
C Code
C Compiler
“snc”
Pre-compiler
Object code

## Slide 8: Advantage
Compiled code. Fast.
Can call any C(++) code
Easy connection to Channel Access and thus Records
  Compared to custom CA client, device support, …
Skeleton for event-driven State Machine
  Handles threading, event handling, …

## Slide 9: Disadvantage
Limited runtime debugging
  See current state, values of variables, but not details of C code within actions
Can call any C(++) code
  and shoot yourself in the foot
Pre-compiler. SNL error
  SNC creates unreadable C code
  Totally cryptic C compiler messages
Risk of writing SNL code
  Starts out easy
  Evolves
  Ends up as a convoluted mess

## Slide 10: Should I use the Sequencer?
Good Reasons:
Start-up, shut-down, fault recovery, automated calibration
Stateful Problem
  My SNL has 20 states, 30 possible transitions, and little C code for each transition
Cannot satisfy system requirements with records
  CALC CALCOUT BO (momentary) SEQ Subroutine records
State machine purpose is to separate control flow and data flow
Bad Reasons:
PID control, interlocks
Warning sign:
  My SNL code has 3 states with 2000 lines of C code
I don’t want to deal with records, I’m more comfortable with C code

## Slide 11: Use the sequencer
For sequencing complex control tasks
E.g. parking and unparking a telescope mirror
Photograph courtesy of the Gemini Telescopes project

## Slide 12: If you really want to use SNL
Good manual:
  http://www-csr.bessy.de/control/SoftDist/sequencer/
Iterate in small steps
  Code a little
  Compile, test
  Code a little more
  Compile, test
When stuck
  Bisect new code into successively smaller sections to find offending statements when diagnostic messages are overly mysterious

## Slide 13: SNL Structure
program SomeName("macro=value")
/* Comments as in C */
/* Options */
/* Variables */
/* State Sets */
Program name!
Used in DBD
&
to launch the sequence.

## Slide 14: SNL Options
option +r; option -c;
Make “re-entrant”. Should be the default. Allows running more than one copy (with different macros).
Start right away, do not await connections. Even with “+c”, the default, PVs may disconnect once you’re running..

## Slide 15: SNL Structure
program SomeName("macro=value")
/* Comments as in C */
/* Options */
/* Variables */
/* State Sets */

## Slide 16: Variables
double pressure;
assign pressure to "Tank1Coupler1PressureRB";
monitor pressure;
short RoughPump;
assign RoughPump to "Tank1Coupler1RoughPump";
string CurrentState;
assign CurrentState to ”{macro}:VacuumState";
int, short, long, char, float, double
Map to channel
Update with channel
string == char[40]
Replaced w/macro’s value

## Slide 17: Array Variables
double pressures[3];
assign pressures to
{
"Tank1Coupler1PressureRB",
"Tank1Coupler2PressureRB",
"Tank1Coupler3PressureRB”
};
monitor pressures;
short waveform[512];
assign waveform to "SomeWaveformPV";
monitor waveform;
Any but ‘string’
Map to channel(s!)

## Slide 18: Event Flags
Declaration:
evflag event_flag_name;
Trigger on Channel Access updates by synchronizing with monitored variable sync var_name event_flag_name; assign var1 “pvname1”; monitor var1; assign var2 “pvname2” monitor var2; sync var1 ef; sync var2 ef;
Communicate events between state sets with efSet(), efTestAndClear(), ef*..

## Slide 19: Event Flags
Multiple PVs may be sync’d with a single evflag but a single PV may not be sync’d with more than one evflag
  Allowed
    sync var1 ef1; sync var2 ef1; sync var3 ef2;
  Not allowed
    sync var1 ef1; sync var2 ef1; sync var3 ef2; sync var1 ef2; # offending statement – attempt to # sync var1 with ef1 and ef2

## Slide 20: SNL Structure
program SomeName("macro=value")
/* Comments as in C */
/* Options */
/* Variables */
/* State Sets */

## Slide 21: State Sets
ss coupler_control
{
state initial{
when (pressure > .0000051){
} state low_vacuum
when (pressure <= .0000049){
} state high_vacuum
}
state high_vacuum{
when (pressure > .0000051){
} state low_vacuum
}
state low_vacuum{
when (pressure <= .0000049){
} state high_vacuum
when (delay(600.0)){
} state fault
}
state fault {
}
}
Starts in First state, name does not matter

## Slide 22: Events
Variable value test
  Variables assigned to PVs and used in events MUST be monitor’ed if their values are changed by external agents alone
when (pressure > .0000051) {
/* Actions … */
} state low_vacuum
when (pressure < 0.000051 && whatever > 7) {
} state high_vacuum
Asynchronous pvGet or pvPut completion
when ( pvGetComplete(someVar) ) { … when ( pvPutComplete(someVar) ) { …

## Slide 23: Events..
Timer expiration
when (delay(10.0)) # This is not an unconditional delay!
{ # It is a timeout that expires only when
} state timeout # other event conditions stay false for
# the specified elapsed time
Event flags
when (efTestAndClear(some_event_flag)) … when (efTest(some_event_flag)) …
/* Meanwhile, in other state */
when (pressure < 0.000051 && whatever > 7) {
efSet(some_event_flag);
} state high_vacuum
Connection state changes
when (pvConnectCount() < pvChannelCount())
when (!pvConnected(some_variable))

## Slide 24: Actions and Transitions
when (pressure > .0000051) {
/* Set variable, then write to associated PV */
RoughPump = 1;
pvPut(RoughPump);
/* Can call most other C code */
printf("Set pump to %d\n",RoughPump);
} state low_vacuum
Action statements mostly resemble C code. Above, RoughPump is a state machine variable. The SNL for the printf is pre-compiled into
printf("Set pump to %d\n", pVar->RoughPump);
SNC adds pVar-> to all state machine variables.
Sometimes inserting manually crafted code blocks is necessary
%{
/* Escape C code so that it’s not transformed */
static void some_method_that_I_need_to_define(double x);
}%
(‘pVar’ is being updated to ‘seqg_var’)

## Slide 25
Walk through the SNL from makeBaseApp –t example
RELEASE.local SNCSEQ = $.../seq-2.2.9
src/Makefile: .._SRCS += sncProgram.st
sncExample.dbd registrar(sncExampleRegistrar)
IOC st.cmd seq sncExample, “user=me”
See /ics/examples/14_seqApp,
/ics/examples/iocBoot/ioc_seq

## Slide 26
program sncExample
double v;
assign v to "{user}:aiExample";
monitor v;
ss ss1 {
state init {
when (delay(10)) {
printf("sncExample: Startup delay over\n");
} state low
}
state low {
when (v > 5.0) {
printf("sncExample: Changing to high\n");
} state high
}
state high {
when (v <= 5.0) {
printf("sncExample: Changing to low\n");
} state low
}
}

## Slide 27: Sequencer Management and Diagnostic Commands
seq NameOfSequence
  Start sequence
seqStop <thread id or name>
  Stop a sequence
seqShow
  List all sequences with IDs and names
seqShow <thread id or name>
  More detail for given thread
seqChanShow <thread id or name>
  List variables of seq

## Slide 28: Sequencer Management and Diagnostic Commands…
seqcar <level>
  Level 0 - show pv statuses
    Total programs=1, channels=18, connected=17, disconnected=1
  Level 1 – show disconnected pvs per program
    Program "sncExample“ Variable "highLev" not connected to PV "one:highLevel“ Total programs=1, channels=18, connected=17, disconnected=1
  Level 2 – show details for each pv by name
    Program "sncExample“ Variable "systemEnable" connected to PV "one:systemEnable“ Variable "pause" connected to PV "one:pause“ Variable "fillTimeout" connected to PV "one:fillTimeout“ . . .

## Slide 29: More…
Support for entry and exit blocks
Assign PV names within code: pvAssign(..)
Get Callback, Put Callback
Checking status & severity of PVs
syncQ to queue received Channel Access updates
and more…

## Slide 30: Summary
SNL and the EPICS sequencer is a powerful tool with a rich feature set
Very easy to implement EPICS state machines with SNL
Read the SNL manual