## Slide 1: Experimental Physics and Industrial Control System Overview
Kay Kasemir
July 2026

## Slide 2: What EPICS looks like
Network Diagram, ~1990
Network Diagram, ~2019
Block Diagram, ca. 2000

## Slide 3: Elec.Eng. Perspective
Oracle
http://xkcd.com/730/

## Slide 4: Experimental Physics and Industrial Control System
Easy, Practical and Intuitive Control System!
Free*, open-source, with documentation, mailing lists, …
https://epics.anl.gov/base/R7-0/6-docs/calcRecord.html
.. as in beer as well as speech
No royalties
Nothing hidden
Modify as you wish
base/…../calc/calcPerform.c

## Slide 5: Antipodean Example

## Slide 6: Australian Square Kilometre Array Pathfinder (ASKAP), Oct. 5, 2012
Juan Guzman, http://www.aps.anl.gov/epics/tech-talk/2012/msg02113.php

## Slide 7: ASKAP User Interface
Juan Guzman, http://www.aps.anl.gov/epics/tech-talk/2012/msg02113.php

## Slide 8: ITER
ITER-FPSC-vBetaVersionPanelsOPI-UserManual.doc, Nadine Utzel, 2011

## Slide 9: ORNL HFIR CG-1D
First EPICS/CSS operation with beam, 2013

## Slide 10: ORNL SNS Beam Lines

## Slide 11: EPICS is not…
One product that you
Install
Run
Done!

## Slide 12: EPICS is a Collaboration
~1989: Started between
  LANL Ground Test Accelerator
  ANL Advanced Photon Source
Until 2004: License agreement required
  LANL registered >150
Now:
  SNS, ANL/APS, BNL, FRIB, SLAC, LANL, JLAB/CEBAF, LBNL, Fermilab D0, Keck & Gemini Telescopes … in the USA
  European Spallation Source in Sweden; Canadian Light Source; DESY, BESSY, .. in Germany; PSI/SLS in Switzerland; Ganil, SACLAY in France; Diamond Light Source and ISIS in England; KEK, J-Parc in Japan; IHEP in China; NSRRC in Taiwan; PLS in South Korea; Australian Synchroton, …
Yearly collaboration meetings
  One each in US and elsewhere
  Typically, >100 people
'Tech-Talk' email reflector usually provides responses within a few hours
  https://epics-controls.org
  Matrix-based chat
Lifetime Achievement Award

## Slide 13: https://epics-controls.org Meetings
Berlin, 1998
Tzukuba, 2000
Chicago, 2018
Oak Ridge, 2016 & 2024
…,
Oxfordshire2025

## Slide 14: EPICS is a Toolkit for distributed control systems
Front-end: “Input/Output Controller” (IOC)
Protocol: Channel Access (PV Access)
Clients: Operator displays, alarm system, …
Mostly Portable: vxWorks, RTEMS, Linux, OS X, Windows

## Slide 15: Distributed
Operator interface
Services: Archive, …
Front-end IOCs
I/O, PLCs, ..

## Slide 16: What an IOC does
Runtime ‘Database’
  Executes records
Known set of ‘Records’
  Read analog value
  Write analog value
  Perform computation
  Control motor
Configuration
  SCAN=1 second
  INP=..what to read..
Serve all via Channel Access or PV Access

## Slide 17: Example: Basic Temperature Control
  Task:
  Read temperature
  Open/close switch as needed
  Repeat
Software?

## Slide 18: Simplistic Code
Sensor temp = connectToSensor(…);
Switch switch = connectToSwitch(…);
Loop:
if (temp.value() < 10) switch.close(); else switch.open();
sleep(1.0);

## Slide 19: That basically works...
Time
Temperature
Desired Temp.
Actual Temp.
Heater on, off, on, off, ...

## Slide 20: What we omitted
Error checking
Code comments
Smoothing of the temperature reading to filter noise
Send current temperature and switch state to network clients (operator display). With units
Attach a time stamp to the data, so that network clients can see for example when the switch was last opened
Send alarm when the temperature is too low or high
Allow runtime changes of the threshold from the remote operator interface
Allow runtime changes to the scan rate
Maybe allow runtime changes to the device address?
What if we have more than one fishtank?

## Slide 21: EPICS 'Database’ for Fishtank
Takes getting used to but handles what we omitted.

## Slide 22: Some Detail on EPICS 'Records'
Programming Configuration
"SCAN=1 second" instead of start thread, delay until next multiple of 1 second, lock required resources, …
"SMOO=0.5" configures the smoothing algorithm.
Almost any field in any record is accessible via network at runtime
  Change scan rate, smoothing, …

## Slide 23: IOC Database
A single record can handle the scanning, signal conditioning, alarming of a temperature, pressure, or similar analog reading.
Combined with binary and computational records, it can express the data flow logic for a front-end computer
  Avoiding the pitfalls of real-time, multithreaded and networked programming.
Can have thousands of records in one IOC.
kHz-rate processing with record chains is doable
  Of course limited by CPU. Not 1000nds of kHz rate-records…

## Slide 24: How fast?
Can be fast or slow, it depends how you use it!
Use the correct tool for the job; Database, custom code (IOC) or custom code (client)‏
Ultimately speed depends upon hardware
Some benchmarks*:
From Andrew Johnson (APS) EPICS Intro slide
2026 Example SNS MPS IOC
60000 records,
8 CPU cores, overall average 2%

## Slide 25: Example Client: Operator Displays
Created in Editor
  No coding, no compilation
Networked
  Open/close
  Multiple OPIs

## Slide 26: EPICS Vocabulary
EPICS Base Code for IOC, database support, basic records, channel access
IOC Input Output Controller, the front-end software
  Hard IOC Using real-time OS running nothing but IOC code
  Soft IOC IOC software just another process on host, typically communicating with networked I/O
Database Executes the EPICS Records
Record EPICS processing block
Device support Code that connects records to hardware Driver
Driver Code that talks to hardware. May be unaware of EPICS
Channel Access, PV Access EPICS network protocols. Expose Channels aka Process Variables

## Slide 27: Information
https://epics.anl.gov https://epics-controls.org
  ’Base’
    ‘Record Reference Manual’
      Everybody Must read!
    ‘EPICS Application Developer's Guide’
      Technical detail about ‘makeBaseApp’, build system, device support, C/C++ API
  ’Modules’, ‘H/W by Manufacturer’
    Look there for device support
  ‘Talk’, ‘tech-talk’
    Primary mailing list

## Slide 28: EPICS Summary
Control System Toolkit
  Distributed, multi-platform, open source, extensible, …
Not fancy, but “works”
  Accelerators, Beam lines, Telescopes, Fusion experiments, …