## Slide 1: EPICS Database
Kay Kasemir
Many slides from Andrew Johnson, APS/ANL
July 2026

## Slide 2: Distributed EPICS Setup
Operator Interface
Input/Output Controller (IOC)
Channel Access (pvAccess)

## Slide 3: IOC
Database: Data Flow, mostly periodic processing
Sequencer: State machine, mostly on-demand
“Hard” IOCs run VxWorks/RTEMS/RT-Linux and directly interface to A/D, D/A, LLRF, … hardware. “Soft” IOCs run on Linux and have no I/O Hardware other than serial or networked devices (Moxa to motor controller, …)
Channel Access, PV Access
LAN
Sequencer
Device Support
I/O Hardware
IOC
Database

## Slide 4: IOC Database
'iocCore' software loads and executes 'Records'
  Configuration of records instead of custom Coding
All control system toolboxes have (better?)
  GUI tools
  Network protocols
  Hardware drivers
  but few have a comparable database!

## Slide 5: Example: Basic Temperature Control
  Task:
  Read temperature
  Open/close switch as needed
  Repeat
Software?

## Slide 6: One Fishy Database
Analog Input Record
Binary Output Record
SCAN Field

## Slide 7: Database = Records + Fields + Links
IOC loads and executes one or more databases
Each database has records
Each record has
  Name (unique on the whole network)
  Type (determines fields and their functionality)
  Fields (properties, can be read, most also written at runtime)
  Often device support to interface to hardware
  Links to other records

## Slide 8: Records are Active
Records ‘do’ things
  Get data from other records or hardware
  Perform calculations
  Check value ranges, raise alarms
  Write to other records or hardware
  What they do depends on record type, field values, device support
… when they are processed
  Records process periodically or when triggered by events or other records
  No action occurs unless a record is processed

## Slide 9: /ics/examples/01_first_steps/very_first.db
# The simplest record that 'does' something
# and produces changing numbers
#
#. softIoc –m S=training –d very_first.db
record(calc, "$(S):random")
{
field(SCAN, "1 second")
field(INPA, "10")
field(CALC, "RNDM*A")
}
Execute: softIoc –m S=training –d very_first.db
Try: help, dbl, dbpr, dbpf
In another terminal: camonitor training:random

## Slide 10: Macros
record(calc, "$(S):random")
{
field(SCAN, "1 second")
field(INPA, "10")
field(CALC, "RNDM*A")
}
Execute: softIoc –m S=demo1 –d very_first.db
In another terminal: camonitor demo1:random
Can have only one “training:random” on the network!
Use macro “$(S)” to create unique names:
S=demo1
S=demo2
…

## Slide 11: Excursion: 04a User Interfaces
Follow those instructions to create display
Set fields ‘PREC’ to 3 and ‘EGU’ to ‘V’


## Slide 12: Record Reference Manual
Current: Link from https://docs.epics-controls.org for each version of EPICS base https://docs.epics-controls.org/projects/base/en/latest/ComponentReference.html#record-type-definitions
Sometimes more convenient: Older “recordref_*.pdf” copy in presentation material

## Slide 13: Record Types
ai/ao: Analog input/output
  Read/write number, map to engineering units
bi/bo: Binary in/out
  Read/write bit, map to string (0 Off, 1 On)
calc: Formula
mbbi/mbbo: Multi-bit-binary in/out
  Read/write 16-bit number, map bit patterns to strings
stringin/out, longin/out, seq, compress, histogram, waveform, sub, …

## Slide 14: Common Fields
Design Time
  NAME: Record name, unique on network!
  DESC: Description
  SCAN: Scan mechanism
  PHAS: Scan phase
  PINI: Process once on initialization?
  FLNK: Forward link
Runtime
  TIME: Time stamp
  SEVR, STAT: Alarm Severity, Status
  PACT: Process active
  UDF: Undefined? Never processed?
  PROC: Force processing
Either
  TPRO: Trace processing, set to 1 to debug record processing

## Slide 15: Record Scanning
SCAN field:
  When processed by other records: “Passive” (default)
  Periodically: “.1 second”, “.2 second”, “.5 second”, “1 second”, “2 second”, “5 second”, “10 second”
  On event: “Event” (EVNT field selects the event), “I/O Intr” (if device support allows this)
PHAS field
  Adds order to records that are on the same periodic scan
    First PHAS=0, then PHAS=1, …
PINI
  Set to “YES” to force record once on startup. Good idea for “operator input” records that are hardly ever changed, so they have an initial value.
PROC
  Writing to this field will process a record

## Slide 16: Database vs. the Rest of the IOC
Channel Access, PV Access
LAN
Sequencer
Device Support
I/O Hardware
IOC
Database
Record scanning runs at higher priority than Channel Access or PV Access
  At high CPU load, PVs might not connect while records are still processed
0.1 second scan runs at higher priority than 10 second scan
PRIO field selects priority for async. completion and event-scanned record
Your mileage might vary
  RTOS or plain Linux?

## Slide 17: Thread Priorities
cd /ics/examples/01_first_steps
Compare
softIoc … as before, epicsThreadShow
sudo ./run_rt.sh, epicsThreadShow
Compare with ‘htop’

## Slide 18: Common Input/Output Record Fields
DTYP: Device type (“stream”, “ether_ip”, …)
INP/OUT: How to read/write, format depends on DTYP
RVAL: Raw value (e.g. 16 bit integer)
VAL: Engineering unit value (e.g. 64bit float)
Output Only:
DOL: Desired Output Link. Output records read this link to get VAL, then write to OUT…
OMSL: .. if Output Mode SeLect = closed_loop
IVOA: Invalid Output Action
DRVL, DRVH: Drive limits of analog output
Is OMSL set to closed_loop? DOL  VAL  OUT Otherwise VAL  OUT

## Slide 19: /ics/examples/01_*/first.db
# Run as
# softIoc –m S=demo –d first.db
#
# A ramp from 0 to 'limit', were limit
# can be configured via a separate record
record(ao, "$(S):limit")
{
field(DRVH, "100")
field(DOL, "10")
field(PINI, "YES")
}
record(calc, "$(S):ramp")
{
field(SCAN, "1 second")
field(INPA, "$(S):ramp")
field(INPB, "$(S):limit")
field(CALC, "A<B ? A+1 : 0")
}
Using ‘output’.
‘input’ would also work, since there’s no hardware to read or write, but only ‘output’ has DRVH…
Reading inputs: A = my own current value
B = value of ..limit record
Which record is scanned?
Use camonitor to show value
Use caput to change limit
Create display
View database in vdct (see vdct presentation, then come back here)

## Slide 20: Analog Record Fields
EGU: Engineering units
PREC: Display precision
SMOO: Smoothing
  VAL = (1-SMOO)*new_value + SMOO*last_value
  SMOO=0: VAL=new_value, default behavior
  SMOO=1: VAL=last_value, defunct behavior
  0<SMOO<1: VAL ‘smoothly’ follows latest reading
LINR: Linearization (None, Slope, breakpoint table)
  EGUL, EGUF, ESLO, EOFF: Parameters for LINR
LOLO, LOW, HIGH, HIHI: Alarm Limits
  LLSV, LSV, HSV, HHSV: Associated alarm severities

## Slide 21: Binary Record Fields
ZNAM, ONAM: State name for “zero”, “one”
ZSV, OSV: Alarm severities

## Slide 22: Links
Input or Output links may be
  Name of other record’s field: “other”, “other.VAL”, “other.A”
    If other record is in same IOC: “Database link”
    If name doesn’t match any local record: “Channel Access link”
  Hardware link
    Details depend on device support
    DTYP field selects device support
    Example formats: “@plc12 some_tag”, “#C1 S4”
Input links may be
  Constant number: “0”, “3.14”. “-1.6e-19”
A record’s FLNK field processes another record after current record is ‘done’

## Slide 23: Database Links
Format: “record.field {flags}”
  VAL is default for field
Flags:
  PP: Process a passive target record
    INP, DOL: Before reading
    OUT: After writing
  NPP: non-process-passive (default)
  MS: Maximize severity (should be the default?)
  NMS: non-MS (default)
  MSS: Maximize Severity and Status
  MSI: .. when severity = INVALID (should be the default?)
Example:
  field(“INP”, “other_rec.VAL PP MS”)

## Slide 24: Channel Access Links
When a linked record is not in this IOC, EPICS automatically uses a Channel Access link
Flags:
  PP: Ignored. Not triggering processing on other IOC
  MS, MSI: Maximize severity (when INVALID)
`dbcar` lists number of (not) connected CA links
`dbcar ””, 1` shows detail of missing links
See the two record in first.db split into first1.db and first2.db
Run both in one IOC, then run them in two IOCs
  Use camonitor to show value
  Use caput to change limit
  Any difference for 1 vs 2 IOCs?
Break a link: caput demo:ramp.INPB bogus What indications do you get?
Why would you split databases into separate files?

## Slide 25: Channel Access Link Flags
CA: Force CA link, even though target in same IOC
  Can be used to break ‘lock sets’
CP: For INP link, process on received CA monitor
  Cause processing when linked value changes. Details depend on MDEL of source.
CPP: CP, but only if SCAN=Passive

## Slide 26: Forward Links
Trigger processing, not passing data
Destination processed if SCAN=Passive
May use CA links
  Must use FLNK=“other.PROC” (other IOC) or FLNK=“other.PROC CA” (same IOC)
  Always triggers processing even for SCAN!=Passive

## Slide 27: Processing chains

## Slide 28: Which record is never processed?

## Slide 29: How often is Input_1 processed?

## Slide 30: How long will this take?
PACT: Processing Active

## Slide 31: Rate Of Change Example
Calculating “Rate-of-Change” of an Input
INPA fetches data that is 1 second old because it does not request processing of the AI record. INPB fetches current data because it requests the AI record to process. The subtraction of these two values reflects the ‘rate of change’ (difference/sec) of the pressure reading.
10 second average:
SCAN=10 second
CALC=(B-A)/10
Should it be
CALC=B-A
?

## Slide 32: /ics/examples/01_first_steps: speed.db
Study speed.db
Use camonitor or display to track rate
What do you get?
Mac Laptop
Training VM on same Mac Laptop…

## Slide 33: Simulation Mode
Input record?
Instead of reading VAL from INP, VAL is now set to SVAL
Either set SVAL directly, or read from SIOL (SIOL  SVAL), SVAL  VAL
Output record?
Instead of writing VAL to OUT link, VAL is written to SIOL
VAL  SIOL
Enable by setting SIMM=1 or YES
Might read SIMM from SIML, for example field(SIML, “SomeGlobalSimEnableRecord”)
More: https://epics.anl.gov/base/R7-0/6-docs/dbCommonInput.html, https://epics.anl.gov/base/R7-0/6-docs/dbCommonOutput.html
Record will be in STAT=SIMM_ALARM with SEVR read from SIMS (default: NO_ALARM)

## Slide 34: Simulation Mode
When in simulation mode, the AO record does not call device support and the AI record fetches its input from the AO record.
Not shown: How are any of these records processed? (SCAN, FLNK, …) How do they read or write when NOT in simulation? (DTYP, INP, OUT)

## Slide 35: Multiple Scan Triggers
Slow Periodic Scan with Fast Change Response
The AI record gets processed every 5 seconds AND whenever the AO record is changed. This provides immediate response to an operator's changes even though the normal scan rate is very slow. Changes to the power supply settings are inhibited by the BO record, which represents a Local/Remote switch.

## Slide 36: /ics/examples/02_simple_control
Study rotation_table.db and display
Study rotation_control.db and display
Basic “Proportional” Control:
What happens if P is too small? … too large?

## Slide 37: /ics/examples/02_simple_control
Study motor_demo.db and display
Study motor_control.db and display
Basic “Integral” Control:
Why does “Proportional” control not work here?
Speed setpoint of 5000 rpm isn’t reached/held. How can you fix this?

## Slide 38: Device Support
Records (AI, AO, ..) on their own only read/write from other records
Device support connects them to hardware
Hardware Device support is outside of EPICS ‘base’. Added to IOC as needed.
DTYP selects a device support module
INP/OUT provides detail

## Slide 39: Synchronous vs. Asynchronous I/O
“Fast”, synchronous device support reads or writes the VAL of a record when the record is processed.
“Slow”, async support starts reading or writing when the record is processed. The record remains in PACT=true state, and device support triggers completion of processing when data has been read/written.
Channel Access ‘get/put’ reads/writes current VAL, no matter if record is processing
Channel Access ‘get/put callback’ will complete once processing completes
Read or write register via VME or PCI bus
Send read-request to networked device, await reply, parse value from received message

## Slide 40: ‘Soft’ Device Support
EPICS base includes DTYP=
“Soft Channel” for AI, AO, BI, BO, ..
  Reads/writes the VAL field
“Raw Soft Channel” for AI, AO, BI, BO, ..
  Reads/writes the RVAL field, converts to/from VAL
“Async Soft Channel” for AI, AO, BI, BO, ..
  Performs a get/put callback, waits for completion

## Slide 41: What could go wrong here?

## Slide 42: Lock-Sets
Group of records connected by links
Processing a record locks its lock-set
  Prevents processing by multiple threads
  Similar but technically separate from PACT
Tends to transparently avoid problems
  .. Unless you are very unlucky.
  Then use “CA” flag to break lock set

## Slide 43: Record Locking vs. PACT
Depending on its device support, a record can “process” for a long time
  Processing sets PACT and triggers driver to fetch data. Some time later driver processes the record again, and clears PACT.
Records in lock-set are locked while
  Processing starts, then again when it completes, but not in the in-between times
  Reading a field
  Writing a field

## Slide 44: Alarms
Common fields:
  SEVR: Alarm Severity
    NONE, MINOR, MAJOR, INVALID
  STAT: Alarm Status
    UDF, READ, WRITE, CALC, HIGH, STATE, …
Binary records:
  ZSV, OSV: Severity for ‘zero’ and ‘one’ state
Analog records:
  LOLO, LOW, HIGH, HIHI: Thresholds
  LLSV, LSV, HSV, HHSV: Associated severities
  HYST: Hysteresis

## Slide 45: Alarm Example
# Raise alarms when temperature near boiling point
record(ai, "$(user):tank")
{
field(DESC,"Water Temperature")
field(SCAN, "…
field(INP, "…
field(EGU, "C")
field(PREC, "1")
field(HIGH, "90")
field(HSV, "MINOR") field(HIHI, "100")
field(HHSV, "MAJOR")
}

## Slide 46: /ics/examples/02_simple_control
Add alarms to motor_demo.db
  MINOR alarm when reaching 4000 or -4000 rpm
  MAJOR alarm at +5000 rpm
How does the display change?

## Slide 47: Monitor Dead-Bands
Analog records send updates to CA/PVA clients
  MDEL Change threshold for most clients, incl. displays
  ADEL .. for archive client

## Slide 48: Record Hints
Use AO, analog output, for user input
  DRVL, DRVH can limit the value range
BO record can be used as timer
  HIGH field: When writing VAL=1, remains 1 for HIGH seconds
  Useful for operator interface buttons: Button writes 1, record reverts to 0 after HIGH=1

## Slide 49: Record Hints
MBBI, MBBO records map states
Define values and states via ZRVL/ZRST, ONVL/ONST, TWVL/TWST, …
Can be used like BI/BO: ZRVL=0, ONVL=1, ZRST  ZNAM, ONST  ONAM
.. For values other than 0, 1: ZRVL=0, ONVL=255
Decode Limit Switch state from bits: ZRVL = 0 ZRST = “Moving” ONVL= 1 ONST=“At Left Limit” TWVL = 2 TWST=“At Right Limit” THVL = 3 THST = “Broken”, THSV=MAJOR
0
Digital I/O Bits
Left limit switch
Right limit switch
1
2
…
5 V

## Slide 50: Record Hints
COMPRESS record can
  Keep last N values in circular buffer
  Compute average, min or max of array
ASUB record can call C code
  INAM, SNAM: Name of initial() and sub()
  Many INP* and VAL* fields
EVENT record can post database event
  Trigger records with SCAN=Event and EVNT=that event

## Slide 51: Record Hints
Use CALCOUT for if-then-else logic
  INP* and CALC as in CALC record
  OOPT “On Change”, “When Zero”, “Transition to Zero” etc.
  Output can either use CALC or a separate OCAL
SEQ, FANOUT, DFANOUT can process a list of records
  Simply process or write values
  SEL can change from processing all to processing selected records

## Slide 52: Calcout Record Details
Combines calc record with analog output functionality
  INPA, INPB, …, INPL and CALC to compute VAL
  OUT to which VAL is written
OOPT determines if/when OUT is written
  “Every Time”, “On Change”, “When Non-zero”, “Transition to Zero”, …
By default, VAL is written, but can also configure
  field(OCAL, “A/B+…”) computes alternate OVAL
  field(DOPT, “Use OCAL”) selects writing OVAL instead of VAL to OUT
 Two calculations and an ‘if’ type selector within one record

## Slide 53: Calcout Example
record(calcout, “Corrector”) { field(SCAN, “.1 second”) field(INPA, “Enable”) field(INPB, “Setpoint”) field(INPC, “Readback”) field(INPD, “17.54”) field(CALC, “A”) field(OOPT, “When Non-zero”) field(DOPT, “Use OCAL”) field(OCAL, “D*(B-C)”) field(OUT, ”SteeringMagnet PP”) }
 CALC to determine if we should do anything, OCAL for computation (proportional control)

## Slide 54: ‘synApps’ Records outside of EPICS base
MOTOR record
  A whole ecosystem for controlling motors
BUSY record can be used to support put-callback
  Some Setpoint record FLNKs to logic that sets BUSY record = 1
  When device reaches setpoint, set BUSY record VAL=0
   CA ‘put-callback’ to setpoint will complete after device reached the setpoint

## Slide 55: Motor Record Details
Record of 100+ fields https://epics.anl.gov/bcda/synApps/motor/motorRecord.html
Basic control
  VAL Desired motor position. Supports put-callback
  RBV Readback value, actual motor position
  DONE Are we done moving the motor?
  HLS, LLS Are we at the high or low limit?
  STOP
Resolution
  MRES, DIR, OFF, EGU… Turn motor ticks into “mm” or “degrees”
  Is it a stepper motor or servo? Do we have an encoder, how is it calibrated?
Motion
  VBAS, VMAX, ACCL, HVEL, JVEL, … Speed, acceleration
  HLM, LLM, … Limits of motion range
  BDST, BACC, RTRY, .. Backlash compensation, retries
More: Homing, “jog”, “tweak”, status,

## Slide 56: Large or small Records?
One Motor Record?
  motor.VAL Setpoint motor.RBV Readback motor.DONE Done? motor.HLS At high limit? motor.MRES Steps per unit …
Collection of Records?
  record(ao, “$(M)_Set”) record(ai, “$(M)_Pos”) record(bi, “$(M)_Done”) record(bi, “$(M)_AtHighLim”) record(ao, “$(M)_StepsPerUnit”) record(waveform, “$(M)_Profile”)
A servo motor doesn’t use steps per unit.
A stepper might support a motion profile
 There is no commonly shared “Power Supply”, “Camera” .. record. Preferred approach is collection-of-records.

## Slide 57: Time Stamps
TIME is generally set to the time when the record last processed
TSE=-2
  Device support already set the TIME, for example to the exact trigger time obtained from hardware
TSE=1…255
  Set TIME to the last occurrence of event 1..255, obtained from timing system
TSEL
  Allows fetching the time stamp from another record

## Slide 58: Linear Conversion
Analog records convert RVAL  VAL
LINR=NO CONVERSION
  VAL = RVAL
LINR=SLOPE
  VAL = (RVAL)*ESLO + EOFF
This assumes device support populates the (integer) RVAL field. If device support already has a floating-point value, it places that in the (double) VAL field.
For additional conversions, then use a CALC record.

## Slide 59: Breakpoint Tables
Analog records can set LINR= typeKdegC with this in a *.dbd file: breaktable(typeKdegC) {
0.000000 0.000000
299.268700 74.000000
660.752744 163.000000
1104.793671 274.000000
1702.338802 418.000000
2902.787322 703.000000
3427.599045 831.000000
...
}

## Slide 60: Summary
Database Records configure the IOC’s data flow
  Fields, links instead of custom code
See
  Record Reference Manual, https://docs.epics-controls.org/projects/base/en/latest/ComponentReference.html#record-type-definitions
  Older IOC Application Developers’ Guide, https://epics.anl.gov/base/R3-15/6-docs/AppDevGuide/AppDevGuide.html
  New documentation, https://epics-controls.org