## Slide 1: EPICS Database Exercises
Kay Kasemir
Many slides from Andrew Johnson, APS/ANL
July 2026

## Slide 2: Extend /ics/examples/01_*/first.db
# A ramp from 0 to 'limit', were limit
# can be configured via a separate record
record(ao, "$(S):limit")
{
field(DRVH, "100")
field(DOL, "10")
field(PINI, "YES")
}
record(calc, "$(S):ramp")
{
field(SCAN, "1 second")
field(INPA, "$(S):ramp")
field(INPB, "$(S):limit")
field(CALC, "A<B ? A+1 : 0")
}
Copy the example: cp first.db exercise.db
Add a “$(S):step” record and use it in the CALC to allow stepping the ramp in increments between 0.1 and 5.
Create a display for all 3 records.
Make the “..ramp” display units of “a.u.” and have it show 2 digits after the decimal point
Add a widget to the display that allows controlling the rate at which the logic processes
Configure the “..ramp” to generate an alarm when the value is above 8
Configure the “..ramp” to only send values to an archive when the value changes by 2 or more
Add an analog output record which, when processed, resets the “..:limit” to 10. Add a button to the display which triggers this reset.

## Slide 3: Binary records
Create a BO with values “Normal” and “Doubled”, add to display
Use in the “..:ramp” to double the effective step size
Configure the BO such that when setting it to “Doubled”, it will revert to “Normal” after 5 seconds

## Slide 4
In the following, we ask you to study a larger example
Read the database files
Understand what each record does
Know the meaning of each field
Get a feeling for the effect of “P” and “I” gains in a PID controller

## Slide 5: Heater Control Simulation
Typical control loop
PID Controller
  O(n) = KP E(n) + KIΣiE(i) dT + KD [E(n)-E(n-1)]/dT
  Update period dT
  Error readings E(n)
  Output O(n)
  Proportional Gain KP, Integral KI, Derivative KD
-

## Slide 6: Study the ”fishtank” example
Go to cd /ics/examples/fishtank
Start IOC: ./st.cmd
Open heater.bob

## Slide 7: No Control
Constant Error
Set the Prop and Int. gain to zero
Verify that tank temperature ignores the Setpoint

## Slide 8: Only Proportional Control
Small residual Error
Set the Prop. gain
Verify that tank temperature reacts to setpoint, but doesn’t quite reach it Why is proportional gain insufficient for heater control?

## Slide 9: Only Integral Control
Eventually, no Error!
.. but Ringing
Set only the Integral gain
Verify that tank temperature reacts to setpoint. Can you find a good value for the int. gain?

## Slide 10: Study database: User Inputs to Simulation
Note use of Macros
Note use of Analog Output for user Input because of DRVL/DRVL
record(ao, "$(user):room")
{
field(DESC, "Room Temperature")
field(EGU, "C")
field(HOPR, "40")
field(LOPR, "0")
field(DRVL, "0")
field(DRVH, "40")
field(DOL, "25")
field(PINI, "YES")
}
record(ao, "$(user):setpoint")
{
field(DESC, "Temperature Setpoint")
field(EGU, "C")
field(HOPR, "0")
field(LOPR, "100")
field(DRVL, "0")
field(DRVH, "100")
field(PREC, "1")
field(DOL, "30")
field(PINI, "YES")
}

## Slide 11: Simulated Tank Temperature
# supervisory: user can adjust voltage
# closed_loop: PID (in separate control.db) sets voltage
# When PID is INVALID, go back to 0 voltage
record(ao, "$(user):heat_V")
{
field(DESC, "Heater Voltage")
field(EGU, "V")
field(DRVL,"0")
field(DRVH,"110")
field(DOL, "$(user):PID MS")
field(OMSL,"closed_loop")
field(IVOA, "Set output to IVOV")
field(IVOV, "0")
}
# ~1100 Watt heater when run with 110V:
# P = U I = U^2 / R, R~12 Ohm
record(calc, "$(user):heat_Pwr")
{
field(DESC, "Heater Power")
field(EGU, "W")
field(INPA, "$(user):heat_V PP NMS")
field(CALC, "A*A/12.1")
}
# Every second, calculate new temperature
# based on current temperature,
# room temperature and heater
#
# A - current temperature
# B - room temperature
# C - heater power
# D - isolation factor (water <-> room)
# E - heat capacity (would really depend on water volume)
#
# Very roughly with
# T(n+1) = T(n) + [Troom-T(n)]*Isolation_factor
# + heater_pwr * heat_capacity
record(calc, "$(user):tank_clc")
{
field(DESC,"Water Tank Simulation")
field(SCAN,"1 second")
field(INPA,"$(user):tank_clc.VAL")
field(INPB,"$(user):room")
field(INPC,"$(user):heat_Pwr PP NMS")
field(INPD,"0.01")
field(INPE,"0.001")
field(CALC,"A+(B-A)*D+C*E")
field(FLNK,"$(user):tank")
}
What causes all these records to process?

## Slide 12: PID (without D) Computation
# Error computation’s SCAN drives the rest
record(calc, "$(user):error")
{
field(DESC, "Temperature Error")
field(SCAN, "1 second")
field(INPA, "$(user):setpoint")
field(INPB, "$(user):tank MS")
field(CALC, "A-B")
field(PREC, "1")
field(FLNK, "$(user):integral")
}
# Integrate error (A) but assert that
# it stays within limits (C)
record(calc, "$(user):integral")
{
field(DESC, "Integrate Error for PID")
field(PREC, "3")
field(INPA, "$(user):error PP MS")
field(INPB, "$(user):integral")
field(INPC, "20.0")
field(CALC, "(B+A>C)?C:(B+A<-C)?(-C):(B+A)")
field(FLNK, "$(user):PID")
}
# PID (PI) computation of new output
# A - Kp
# B - error
# C - Ki
# D - error integral
record(calc, "$(user):PID")
{
field(DESC, "Water Tank PID")
field(PREC, "3")
field(LOPR, "0")
field(HOPR, "110")
field(INPA, "10.0")
field(INPB, "$(user):error MS")
field(INPC, "5.0")
field(INPD, "$(user):integral MS")
field(CALC, "A*B+C*D")
}

## Slide 13: Add Differential Control
”Patch” database
How does it change the processing of records?

## Slide 14: Adding Differential Control
Lower over/undershoot