## Slide 1: EPID Record
Kay Kasemir
July 2026

## Slide 2: PID Control: Old but still prevalent
Typical control loop
PID Controller
  O(n) = KP E(n) + KIΣiE(i) dT + KD [E(n)-E(n-1)]/dT
  Update period dT
  Error readings E(n)
  Output O(n)
  Proportional Gain KP, Integral KI, Derivative KD
-
Basic Recipe
Increase KP until system oscillates, back off a little
Increase Ki to eliminate residual error
Maybe use KD to dampen overshoot
See also “Ziegler-Nichols” and many control system theory books

## Slide 3: Why does EPICS base not include a PID record?
How to define?
  P, I, D gains with O(n) = KP E(n) + KIΣiE(i) dT + KD [E(n)-E(n-1)]/dT?
  Kp applied to all terms? O(n) = KP(E(n) + KIΣiE(i) dT + KD [E(n)-E(n-1)]/dT)?
  P gain Kp, Integration time Ti=Kp/Ki, Derivative time Td=Kd/Kp?
Avoid integral windup?
  Limit abs(error sum) < max
  Reset error sum whenever setpoint changes
    Start over for new setpoint
  Reset error sum when error > “Integration Zone”
    Only use Ki to fine-tune once error is small, within IZone
 Collection of CALC records, original PID record, “Controlled” CPID record, “Enhanced” EPID record

## Slide 4: EPID Record
Included in APS synApps “std” module
VAL is the setpoint
INP reads current value
Error sum limited to [DRVL, DRVH]
Applies KP, KI, KD gains as output= KP(err + KI sum + KD diff)
FBON=1 to enable feedback
Output is limited to [DRVL, DRVH]
Writes to OUTL

## Slide 5: About the example
Showing EPID record now as follow-up to PID-using-CALC
.. but EPID record is not included in EPICS base, i.e., unknown to the “softIoc” we used so far!
Usage of “makeBaseApp.pl” to create IOCs with additional modules will be detailed later

## Slide 6: Example
record(epid, "$(S):pid")
{
field(DESC, "PID controller")
field(EGU, "deg")
field(PREC, "1")
field(SCAN, ".1 second")
field(INP, "$(S):angle")
field(KP, "0.5")
field(DRVL, "-12")
field(DRVH, "12")
field(OUTL, "$(S):voltage PP")
}
IOC
cd /ics/examples/02b_epid
cat pidApp/Db/rotation_control.db
﻿cd iocBoot/iocpid
./st.cmd
Display
In CSS, File/Open ﻿/ics/examples/02b_epid/rotation_control.bob
Turn feedback “On”, change setpoint, tweak P, I, D

## Slide 7: ‘EPID’ Record
Currently the preferred EPICS PID record
For more, see
  https://github.com/epics-modules/std
  https://github.com/epics-modules/std/blob/master/docs/epidRecord.md