## Slide 1: Channel Access Security Lab
John Sinclair, Kay Kasemir
July 2026

## Slide 2: Plan
  Run a database with “..:ramp” and “..:limit” records
  Note that there are no restrictions on modifying ..:limit
  Reconfigure the IOC to use access security
  Assert that only user “expert” may modify the above PV when security is enabled
  Disable access security and verify no restrictions

## Slide 3: Open two terminal windows
  Window 1 – run IOC
    cd /ics/examples/10_casecurity
    Read database and run it
    gedit demo.db &
    softIoc –m S=demo –d demo.db
  Check who’s connected
    casr 1
  Verify that there is no acc.sec.
    asdbdump
  Window 2 – access it
    camonitor demo:ramp
    Ctrl-C to stop camonitor, then
    caput demo:limit 5
    Note that write succeeds
    caget demo:limit
    camonitor demo:ramp

## Slide 4: Add Access Security
  Window 1 – run IOC
    cd /ics/examples/10_casecurity
    Check what we’re running
    gedit secure.acf &
    softIoc –m S=demo –d demo.db –a secure.acf
  Check who’s connected
    casr 1
  Verify that acc.sec. rules are defined
    asdbdump
  Window 2 – access it
    camonitor demo:ramp
    Note that write still succeeds
    caput demo:limit 5
    caget demo:limit
    camonitor demo:ramp
  Explain why!

## Slide 5: Enable Access Security
  Window 1 – Update databse & run IOC
    cd /ics/examples/10_casecurity
    Check “ACF” comments in demo.db, compare to solution.db
    softIoc -m S=demo -d solution.db -a secure.acf
  Check who’s connected
    casr 1
  Verify that acc.sec. rules are defined
    asdbdump
  Window 2 – access it
    camonitor demo:ramp

## Slide 6: Enable Access Security .. and test it
  Window 2
    Verify that the “training” user can no longer write
    caput demo:limit 5
    Change the mode, check we can write in that state
    caput demo:accessState 1
    caput demo:limit 5
    Back to normal
    caput demo:accessState 0
    caput demo:limit 10

## Slide 7: Enable Access Security .. and test it
  Window 2
    Change to ”expert” (password is $expert), check if that user can write
    su expert
    caput demo:limit 5
    Check if that is independent from the “demo:accessState”

## Slide 8: Check with GUI
  Create a display or use solution.bob.
  Note how the text entry for demo:limit changes based on mode

## Slide 9: Note
We used ‘softIoc’ and its ’-a /path/to/config.asg’ option.
Run with added option ‘-v’ to see what would go into the st.cmd of a makeBaseApp IOC
  ﻿$ softIoc -v -m S=demo -a secure.acf -d solution.db … asSetSubstitutions("S=demo") asSetFilename("secure.acf") … dbLoadRecords("solution.db", "S=demo") iocInit()