## Slide 1: EPICS Database Updates
Kay Kasemir
Many slides from Andrew Johnson, APS/ANL
July 2026

## Slide 2: Comparably New Database Features
Wildcards for ‘patch’ databases
Long Strings
JSON Notation for links and subscriptions
PVA links

## Slide 3: ‘Patch’ Database
Database files can modify fields of existing records or add new fields/records
ps.db limit.db st.cmd
record(ai, “voltage”) { field(DTYP, … INP … field(SCAN, “2 second”) field(FLNK, ”current”) }
record(ai, “current”) { field(DTYP, … INP … field(FLNK, ”power”) } record(calc, “power”) { field(INPA, “voltage”) field(INPB, “current”) field(CALC, “A*B”) }
record(bo, “ps_enable”) …
record(ai, “voltage”) { field(SCAN, “.1 second”) } record(calc, “power”) { field(FLNK, “limit”) } record(calcout, ”limit”) { field(INPA, “power”) field(CALC, “A < 100”) field(OUT, “ps_enable”) }
dbLoadRecords “db/ps.db”
dbLoadRecords “db/limit.db”
Organize records.
“ps.db” can be used standalone, or with “limit.db”.
Order of loading *.db files matters!

## Slide 4: ‘Patch’ Database …
Note that the record type cannot be changed. Must use the correct record type, or “*” to patch any type
ps.db limit.db
record(ai, “voltage”) { field(DTYP, … INP … field(SCAN, “2 second”) field(FLNK, ”current”) }
record(ai, “current”) { field(DTYP, … INP … field(FLNK, ”power”) } record(calc, “power”) { field(INPA, “voltage”) field(INPB, “current”) field(CALC, “A*B”) }
record(bo, “ps_enable”) …
record(ai, “voltage”) { field(SCAN, “.1 second”) } record(“*”, “power”) { field(FLNK, “limit”) } record(calcout, ”limit”) { field(INPA, “power”) field(CALC, “A < 100”) field(OUT, “ps_enable”) }
In this example, the patch database doesn’t care if “power” is an ai, ao, calc, calcout, ..
Error when record("*"… is unknown asserts correct order of loading *.db files.
In st.cmd, option to require “*” for overloads:
var dbRecordsOnceOnly 1
See /ics/training/examples/fishtank, tank.db is patched by control*db

## Slide 5: Long Strings
Unfortunately, EPICS ‘STRING’ was initially defined as CHAR[40]
Channel Access uses DBF_STRING = CHAR[40]
Record names, INP/OUT links can now be much longer
  field(INPA, "SomeReallyLongRecordNameThatExceeds40Characters PP MS")
..but you cannot read/modify them via channel access?!

## Slide 6: Old Workaround
Use record(waveform, "chars") { field(DESC, "Character waveform for long string") field(FTVL, "CHAR") field(NELM, "200") }
.. and (!) tell client that CHAR[] is not meant to be BYTE[] but long STRING. caget -S …., Format: String in operator interface tools
See /ics/examples/11_long_strings/strings.db and display

## Slide 7: New Workaround
IOC turns any string for VAL, INP, DOL into long-string CHAR[] if PV name ends in ‘$’
Long-String input and output records “lsi” and “lso” default to VAL of type STRING, but VAL$ becomes CHAR[]
Clients still need to be told if CHAR[] is BYTE[] or long string!
  caget some_lsi_record  DBR_STRING, only 40 chars
  caget some_lsi_record.VAL$  DBR_CHAR[], shown as numbers
  caget –S some_lsi_record.VAL$  Yay!
See /ics/examples/11_long_strings/strings.db and display

## Slide 8: JSON: “JavaScript Object Notation”
Standard text syntax to represent structured data
EPICS starts to use it to provide details for links
{ number: 3.14, text: "Hello!", substructure: { numbers: [1, 2, 3, 4] } }

## Slide 9: JSON Notation for INP links
New support for JSON notation allows providing more detail
First practical use: {const:…}
  record(lsi, "lsi_init") { field(SIZV, "500") field(INP, {const:"Hello, this is a string and it can be really long!”}) field(PINI, "YES") } record(waveform, "array") { field(FTVL, "CHAR") field(NELM, "200") field(INP, {const:[65, 66, 67, 68, 69]}) field(PINI, "YES") }
See /ics/examples/11_long_strings/strings.db and display

## Slide 10: JSON Notation for Subscription Filters
In one window, run
  cd /ics/examples/01_first_steps ﻿softIoc -m S=demo -d first.db
In other window, compare the following camonitor demo:limit camonitor 'demo:limit.{ts:{}}' (run several times…)
  camonitor demo:ramp camonitor 'demo:ramp.{dbnd:{abs:1.9}}'

## Slide 11: JSON Notation for Network links
Database Link
  field(INP, "SomeRecordInSameIOC")
Network = Channel Access Link
  field(INP, "SomeRecordInSameIOC CA")
  field(INP, "SomeRecordInOtherIOC")
Network = PV Access Link field(INP, {pva:{pv:"SomeRecord”}})
For the longest time, ”Network Links” used the only protocol available, Channel Access.
Now, there is a way to force PVA Links.
Eventually, there should be an IOC option like
EPICS_NETWORK_LINK_DEFAULT=CA/PVA

## Slide 12: More likely to come
Extensible links https://epics.anl.gov/base/R7-0/8-docs/links.html
Channel filters https://epics.anl.gov/base/R7-0/6-docs/filters.html