## Slide 1: Put- and Get-callback (aka completion) Support, ‘Busy’ Record
Kay Kasemir
July 2026

## Slide 2: Basic Automation Example
Move motor to some position
Open shutter
Take data for 5 seconds
Close shutter
Has the motor reached the position?
How quickly does the shutter open?

## Slide 3: What not to do
Ask motor to move to position X
Wait until motor encoder reports X0.1mm
Ask shutter to open
Wait 4 seconds - Fred said that’s how long it’ll take
Take data for 5 seconds
Close shutter
Not reliable!

## Slide 4: Based on readback, are we there, yet?
Time
Temperature, Position, …
Setpoint
Readback
done?
done?
done!

## Slide 5: IOC has to tell us when it’s done!
Use CA “put-callback”
Record completes callback when it is “done”
Requires record with support for “completion” aka “put-callback”
Motor record: When reaching desired position
Other record: Check device support manual
Plain database: Use BUSY record

## Slide 6: Does “SomeRecord” support put-callback?
Hard to tell from outside
  No? “put-callback” will return right away like a plain “put”
  Yes? “put-callback” will return when record is done, which could be after 0.01 sec (fast shutter) or hours (cryostat cooling down)…
Device support manual tells you that put-callback is supported?
  Good! Motor record, some temperature controller device support, …
BUSY record allows you to create record logic that supports put-callback

## Slide 7: Internals: EPICS record PACT field
PACT is binary flag that is 1 (ON) when record is processing
CA put-callback is mechanism to use PACT information…
…and not return until PACT is 0 (OFF)
caput -c -w timeout PV value
caput –c –w 20 SomeMotorRecord 5.7

## Slide 8: BUSY Record to support Put-Callback
done
VAL = 1 ”Busy”, VAL=0 “Done”
Blocks processing (PACT=1) while busy
Busy record
VAL=1
VAL=0
Record A
caput –c …
write
Link
done
More records,
or SNL code

## Slide 9: Typical Use
Writing to some record, which has FLNK or OUT links to a busy record, sets busy.VAL = 1
This causes writer to that first record to block in put-callback
Something else resets busy.VAL = 0
  Other database logic
  Sequencer code
  asyn device support
  …
Put-callback completes

## Slide 10: Monitor, active Get, Get-Callback
Typical client should use ‘monitor’ to efficiently receive the most recent value
  PyEPICS caget() does this by default
But consider this:
  We monitor “SomePV”, last received value was 10
  caput(SomePV,11)
  We should real soon receive an update with value 11, but until then PyEPICS caget(“SomePV”)will return 10
   Sometimes you need to force an active, round-trip “caget”, not rely on the next monitor. In PyEPICS: caget(“SomePV”, use_monitor=False)
There is also “get callback” that will cause record to process, wait for completion, then return the current value

## Slide 11: Put-Callback (and sometimes round-trip get or get-callback)
.. Is essential for robust automation
Check if your device support offers callback/completion
If not, use BUSY record to create database logic that supports put-callback