## Slide 1: PVA Gateway
Kay Kasemir
July 2026

## Slide 2
Examples will use the PV Access Gateway, https://epics-base.github.io/p4p/gw.html
The Channel Access Gateway is similar, https://epics.anl.gov/extensions/gateway/,

## Slide 3: PV Access or Channel Access 101
CSS, pvget, …
IOC
Client
Server
Search, connect, read, write

## Slide 4: Gateway Principle
CSS, pvget, …
IOC
Gateway
Client
Client
Server
Server
Certain miracles are possible right there…

## Slide 5: Why? Bridge Networks!
  Gateway on computer w/ multiple network connections. Maybe in DMZ.
Gateway
Client
Client
Server
Server
Network 2
Network 1

## Slide 6: Why? Access Control!
Gateway often ‘read only’
Gateway
Client
Client
Server
Server
Control System Network
Big Bad Wild World Network
Client
Inside network, clients have full access

## Slide 7: Why? Reduce network load!
IOC
  Gateway buffers connections and values.
  Clients disconnect from GW
  GW keeps its connection for a little while. Reduced search requests, IOC connects/disconnects
Gateway
Client
Client
Server
Server
Client
Client
Client
Control System Network

## Slide 8: Configuration
Read from where?
  Like EPICS_CA_ADDR_LIST resp. EPICS_PVA_ADDR_LIST
Serve to whom?
  Network interfaces on which to run server
  PVA/CA security
Other
  Publish GW status via extra PVs?
  Transform PV names?

## Slide 9: Example: Standalone Demo
All on ’localhost’
Gateway
pvget/put/monitor 2
Client
Server UDP: 5086
IOC UDP: 5076
pvget/put/monitor 1

## Slide 10: Example
Start a PVA server cd /ics/examples/15_pvaccess python 4_server.py
Connect to it the normal way, note how it uses port 5076 to search for the PVA server EPICS_PVA_DEBUG=100 pvget demo:value
Read gateway.conf, start it pvagw –v gateway.conf
Try examples mentioned in gateway.conf export EPICS_PVA_AUTO_ADDR_LIST=NO export EPICS_PVA_ADDR_LIST=127.0.0.1:5086 pvmonitor demo:value pvput demo:limit 40

## Slide 11: More..
Everything you ever wanted to know
  https://epics.anl.gov/extensions/gateway/index.php or
  https://epics-base.github.io/p4p/gw.html