## Slide 1: Alarm System
July 2026
Kay Kasemir

## Slide 2: EPICS PVs carry Values with Alarm Information
IOC 1
IOC 2
PV
VAL: 20
HIHI: 20
HHSV: MAJOR
PV
VAL: 10
HIGH: 5
HSV: MINOR
No alarm, MINOR, MAJOR
  Analog records: LOLO, LOW, HIGH, HIHI limits
  Binary records: 0 or 1 state may alarm
Display Tools
  Typically indicate alarm state via border and/or color

## Slide 3: Alarm Fields in EPICS Records
# bi, bo﻿
record(bi, "binary")
{
# Alarm states
field(ZSV, "MINOR")
field(OSV, "MAJOR")
# Display niceties
field(ZNAM, "Marginal")
field(ONAM, "Hopeless")
}
﻿record(mbbi, "states")
{
# Alarm states
field(TWSV, "MAJOR")
# Display niceties
field(ZRST, "Off")
field(ONST, "On")
field(TWST, "Overheated")
}
/ics/examples/22_alarms/alarms.db and alarms.bob

## Slide 4: Alarm Fields in EPICS Records
# ai, ao, calc, calcout, longin, longout, …﻿
record(ai, "analog")
{
# Alarm limits
field(HIHI, "100")
field(HHSV, "MAJOR")
field(HIGH, "80")
field(HSV, "MINOR")
field(LOW, "20")
field(LSV, "MINOR")
field(LOLO, "0")
field(LLSV, "MAJOR")
# Alarm hysteresis
field(HYST, "5")
# Display niceties
field(HOPR, "110")
field(LOPR, "-10")
field(EGU, "Fathoms")
field(PREC, "1")
}
For historic reasons, need to set both
one or more alarm threshold
corresponding severity
/ics/examples/22_alarms/alarms.db and alarms.bob

## Slide 5: Alarm Fields in EPICS Records
record(ai, ”only_hihi")
{
field(HIHI, ”100")
field(HHSV, ”MAJOR")
}
record(ai, ”only_high")
{
field(HIGH, "80")
field(HSV, "MINOR")
}
record(ai, ”only_low")
{
field(LOW, ”10")
field(LSV, "MINOR")
}
Perfectly fine
Don’t do this
record(ai, ”high_as_hihi")
{
field(HIGH, ”100")
field(HSV, ”MAJOR")
}
record(ai, ”odd_order")
{
field(HIHI, ”100")
field(HHSV, "MINOR")
field(HIGH, "80")
field(HSV, ”MAJOR")
}
/ics/examples/22_alarms/alarms.db and alarms.bob

## Slide 6: Fishtank
Is tank temperature above 70 C or below 0 C a good alarm?
Is heater at 110 V a good alarm?
/ics/examples/fishtank: st.cmd, heater.bob

## Slide 7: EPICS PVs carry Values with Alarm Information
IOC 1
IOC 2
PV
VAL: 10
HIGH: 5
HSV: MINOR
No alarm, MINOR, MAJOR
  Analog records: LOLO, LOW, HIGH, HIHI limits
  Binary records: 0 or 1 state may alarm
Display Tools
  Indicate alarm state via border
What if nobody is looking at the screen at the time?
PV
VAL: 20
HIHI: 20
HHSV: MAJOR

## Slide 8: Alarm System Idea
Alarm System
Indicate alarms: Which PV? When? What value?..
Guidance
Related Displays
Keep alarms until acknowledged & cleared
PV
VAL: 20
HIHI: 20
HHSV: MAJOR
“Check XYZ.
Try opening ABC.
Call Fred.”
PV
VAL: 10
HIGH: 5
HSV: MINOR

## Slide 9: Implementation
Alarm Server
Monitors PVs, updates current state
PV
PV
PV
PV
Apache Kafka
Alarm Configuration - Which PVs to monitor - Guidance - Display Links
Current State - Which PVs are in alarm?
CS-Studio Alarm UI
For details of implementation, see CS-Studio Alarm System Based on Kafka,
https://accelconf.web.cern.ch/icalepcs2019/papers/wesh2001.pdf

## Slide 10: Initial Setup
https://github.com/ControlSystemStudio/phoebus/blob/master/app/alarm
Install Kafka (typically as Linux service)
Check that “Accelerator” config exists cd /ics/tools systemctl status kafka ./monitor_topics.sh Accelerator
Start alarm server (typically also as Linux service) alarm-server

## Slide 11: Configuration for ‘Fishtank’
Open CS-Studio Applications, Alarm, Alarm Tree
Find component “Fishtank”
  Check Guidance and Display link

## Slide 12: Configuration Example
Right-click on “Fishtank”, Add Component
  PV “training:heat_V”
  Description
    Anything’s better than the PV name
  Specific Guidance and Displays
    Should have guidance. Otherwise, why is this an alarm?
  Enabled? Latch? Annunciate?
    Usually: Yes, otherwise: Why bother?
  Delay?
    Hack for noisy alarm trigger PVs
  Automated Actions
    mailto:fred@google.com

## Slide 13: Example Alarm Workflow
Cause an alarm
  caput epics-dev:setpoint 72
Inspect Alarm
  Watch as alarm is indicated
  Open associated display
Handle It
  Acknowledge
  Reduce setpoint
   Clear
Suggested “Alarm” layout:
Alarm Tree to the left,
Alarm Table at the bottom,
both “locked”

## Slide 14: Alarm Tree
Primary configuration tool
Hierarchical
  Guidance, Displays apply to sub-nodes
Operational useful to
  Check if numerous alarms originate in the same area
  Acknowledge or disable complete subtrees

## Slide 15: Alarm Table
Primary operations tool
Ideally empty
View/sort/acknowledge alarms
Open guidance and displays

## Slide 16: Alarm Area Panel
Useful for ‘Overview Displays’
Indicates ‘across the room’:
All OK?

## Slide 17: Alarm Annunciator
Annunciates the description of alarms
Basic “heads up” to check alarm table for details

## Slide 18: Basic Roles
System Expert
  Provide useful alarm levels
  Explain what to to when alarm happens
Control System Engineer
  Configure alarm levels
  Maybe create new alarm trigger PV
  Create displays
Operations Expert
  Add alarm trigger PV to alarm system, with guidance and links to displays
Operators
  Handle alarms, helped by guidance

## Slide 19: Alarm System
Alarm Server monitors PVs, tracks alarms
Alarm Tree to configure
  PV?
  Guidance?
  Displays?
Alarm Table, Area Panel, Annunciator to use
  Acknowledge
  Open Displays
Suggested Layout with “locked” alarm panels